## Slide 1: BLRBAC Vancouver Nov 15-2023 Aircheck
Gus Vergel
Industrial Applications and Clean Air Advisor
g.vergel@bgecleanair.com

## Slide 2: Gas-Phase Filtration Solutions
Agenda:
  Equipment to protect
  Cost of a Board
  Microscopic Corrosion
  Metals to protect
  Current Situation:
    Identify
    Quantify
    Analyze
  Corrosion Aids
    Indicators or Monitors?
    Specialty HVAC
    Media Longevity
    Equipment

## Slide 3: Equipment to Protect
VFD’s, PLC’s, DCS IO Boards, Field Instruments, Integrated Circuit Boards ICB’s, Printed Circuit Boards PCB’s, Servers, Magnetic Recording Media, Switches, Relays, Contacts, etc.
5 Dollar Fuse Story!!!!!

## Slide 4: Protect your equipment from…….?
Moisture
Corrosive Gases
Oxygen
Particulate

## Slide 5: Cost of a Board
We all have dealt with electronic board failures from our house to our vehicles.
Boards are on the range of 2K to 20-30K.
Downtime
Production Losses
Nowadays the cost of a board could be considered priceless if we are Careless.

## Slide 6: Microscopic Corrosion
< 0.03 micron per year.
Gas Phase Filtration is the most effective and practical method to remove or reduce the concentration of Corrosive gases.

## Slide 7: Metals to protect
Silver
Gold
Copper
The passage of lead-free (RoHS) Restriction of Hazardous Substances in Electrical and Electronic Equipment manufacturing regulations for all electronic equipment has placed a greater emphasis on the control of corrosive gases.
Lead-free products with a silver surface finish will corrode in high sulfur environments.

## Slide 8: Current Situation. From Consequence to Cause!
Identify all electronic boards replaced over the last 2-3 years.
Quantify the (Cost, labour, downtime)
Analyze each defective board based on the following:
  Location : (Bleach Plant, Control Room, etc.)
  Sub-location: (MCC, Control Room, Data Center, etc.)
  State of “Control Room” (AIRCHECK)
    Doors, ceiling, roof, conduit cables sealed.
    Airlocks state
    Air Conditioning Maintains 20-21C / 70F
    Humidity : 42 % RH
    Is the AHU/Scrubber working properly, maintained and equipped with the adequate media and filters?

## Slide 9: Corrosion Aids
Indicators or Monitors?
  Reactivity Monitoring Coupons: This passive method is an indicator of corrosion that uses a pre-measured and weighted piece of silver or copper to be exposed in the corrosive environment.
  Active Monitoring System: This method is and electronic device that involves constant feedback of data measuring the type and level of corrosion, temperature, humidity, and room pressure.

## Slide 10
Rep Name
Address
Contact info

## Slide 11: Specialty HVAC
AHU and/or Scrubbers?
  The combination of Both
  Sequence:
    Screen
    Demister (Droplet separators)
    Prefilter MERV 8, 9
    Media
    Post Filter MERV 13, 15
MERV: Minimum Efficiency Report Value

## Slide 12: Media Longevity

## Slide 14: Media and Equipment
Modules Easy to replace molecular media cassettes with sampling ports, and our patented Posi-Track™ technology.
Bulk Media
Media available in 36x37x48 poly lined sling bags or 1ft3 corrugate boxes for bulk applications.

## Slide 15: BGE Over 50 Years Providing Indoor Air Quality to all Industries.